Section D, Rev. 3, 11/25/03
NC150R—Area of Rescue Assistance System


Engineers’ Specification

1.0 General

A.
The contractor shall provide and install all equipment, accessories and materials necessary for a complete operating system in accordance with the following specifications. 

B.
The equipment furnished under this specification shall be the standard product of one manufacturer and shall be as manufactured by TekTone® Sound & Signal Mfg., Inc.

C.
The contractor shall guarantee availability of local service and available stock of the manufacturers standard parts. 

D.
The contractor shall be responsible for providing a complete functional system including all necessary components whether included in this specification or not.

Part 2—System Configuration and Operation

2.1 Configuration

The system shall consist of remote stations (IR150 series), audio-visual annunciator (NC150R), and power and control equipment (IH151NK) all as specified herein and as shown on the plans. 

2.2 Operation 

A call may be originated at the remote station by pressing the call button on the faceplate. This shall cause the following: 

A.
The call placed amber light on the station shall illuminate

B.
The annunciator lamp/selector button and call lamp shall light steady on the master annunciator panel

C.
A slowly pulsing audible tone shall sound
D.
To answer the call, the appropriate lamp/selector button is depressed and the operator may talk via the speaker and talk button. The person at the remote station may answer hands free

Part 3—Equipment

3.1 Remote Stations 

Architect/Engineer: Select one of these three remotes: IR150SS Stainless Steel, IR150N Aluminum, or IR150B ABS Plastic.

A.
IR150SS Stainless Steel Remote Station:

1.
The remote station shall contain an amber “call-placed” indicator and a red acknowledge indicator, a 3.5" 45ohm speaker and a cancel button on a stainless steel panel

2.
Screw terminals shall be provided for wire connections

3.
Stations must be mounted no higher than 48" off the finished floor

4.
The remote station shall be TekTone® IR150SS

5.
Housing required shall be TekTone® OH600

B.
IR150N Aluminum Remote Station:

1.
The remote station shall contain an amber “call-placed” indicator and a red acknowledge indicator, a 3.5" 45ohm speaker and a cancel button on a extruded aluminum panel

2.
Screw terminals shall be provided for wire connections

3.
Stations must be mounted no higher than 48" off the finished floor

4.
The remote station shall be TekTone® IR150N

5.
Housing required shall be TekTone® IH106N

C.
IR150B ABS Plastic Remote Station:

1.
The remote station shall contain an amber “call-placed” indicator and a red acknowledge indicator, a 2.5" 45ohm speaker and a cancel button on a ABS plastic panel

2.
Screw terminals shall be provided for wire connections

3.
Stations must be mounted no higher than 48" off the finished floor

4.
The remote station shall be TekTone® IR150B

5.
Mounting requirement is a three-gang ring

3.2 Remote Call Indicator: (optional)

A.
The remote call indicator shall contain a bulb with a translucent plastic cover mounted on a two gang, plastic faceplate®
B.
The white cover shall be removable without the use of tools and the bulb shall be bayonet mount to allow ease of bulb replacement

C.
The remote call indicator shall be TekTone® LI381

3.3 Remote Tone Light Indicator: (optional)

A.
The remote tone light indicator shall contain a tone signaling device and a “call” indicator LED mounted on a single gang, ABS plastic faceplate.

B.
Wiring shall be via plug-in connector

C.
Call indications shall be a steady LED and tone every 8 seconds

D.
The remote tone light indicator shall be TekTone® LI150B

3.4 Central Audio Visual Annunciator Unit

A.
The central annunciator unit shall contain an individual lamp/selector button corresponding to each calling location

B.
Additionally it shall contain a tone signaling device, lamp test button, call and talk push buttons, a 3.5" 45ohm speaker and integral voice amplifier

C.
Indicator lamps shall have removable lenses for lamp replacement and to protect lamp identification markings.

D.
Construction shall be of extruded aluminum with a metal flush mount wall housing and trim frame.

E.
Screw terminals shall be provided for wiring connections

F.
The central annunciator shall be TekTone® NC150R for up to 8 remote stations. Any quantity of remotes may be accommodated by selecting a larger annunciator unit (Contact factory for part numbers)

G.
The NC150R housing shall be TekTone® OH150

3.5 Operational Placard

The operation instructions sealed in plastic shall be mounted adjacent to each IR150 series remote. See Appendix A.

3.6 Power Supply/Control Unit

A.
The annunciator power supply/control unit shall consist of:

1.
24VAC 30VA transformer (SS106)

2.
Power Supply and control circuits (PK151A)

3.
12" × 12" swing door cabinet (IH151N)

B.
The supply/control unit shall be TekTone® IH151NK and be assembled with the above described parts

Part 4—Wiring

Wiring shall be in strict accord with TekTone® Installation Manual IL591

Part 5—Warranty

Each piece of equipment shall be warranted by the equipment manufacturer to be free of defects in material and workmanship for a period of twelve (12) months from the date of shipment from the factory. The equipment supplier shall provide a full year of warranty on the entire system, including on-the-premises maintenance service during normal working hours at no cost to owner for parts or labor except for damage resulting from accident, misuse, abuse or Act of God.

Part 6—Shop Drawings

The electrical contractor shall submit shop drawings to the electrical engineer for approval. The contractor must have approved shop drawings in his possession before installation.

Appendix A

FOR EMERGENCY ONLY

Area of Rescue Assistance

Operating Instructions

1.
Push the call button for help.


2.
Observe the amber call-placed light and 



remain in this designated area.


3.
Observe the red acknowledge light and 



listen for instructions.


4.
Answer voice communication (hands-free)

Website Disclaimer and Legal Notice for downloadable 
Architects & Engineers Specifications

The specifications attached herein are being supplied in a text format for your convenience. TekTone® Sound & Signal Mfg., Inc. is not responsible for any changes made to the original documents.

As with any other TekTone® Sound & Signal Mfg., Inc. document, please be advised that the information was prepared by TekTone® Sound & Signal Mfg., Inc. as general information and a service to our customers. While we endeavor to supply accurate information, we can take no responsibility for errors or misinterpretations in any of the content of this site. We also reserve the right to remove or change literature and pages from this site where legal requirements are contravened or where complaints are received and upheld.

Except in the case of third-party material reproduced on this site, the information and all content, including logos and artwork, provided herein is protected under the U.S. and Foreign Copyright Laws and may not be copied, reproduced or retransmitted by any means, electronically or otherwise, without the express written permission of TekTone® Sound & Signal Mfg., Inc.

Modifications. All modified specifications will include the following ledger: Modified specifications are based upon TekTone® Sound & Signal Mfg., Inc. product specifications. Modified specifications have not been reviewed or approved by TekTone® Sound & Signal Mfg., Inc., unless so noted.

Indemnification. It is agreed that TekTone® will be held harmless from any claims, causes of action, pending or threatened, losses, awards, damages or attorney’s fees arising out of any suit or claim relating to the use and/or modification of the specifications.

Reservation of Rights. This disclosure is not intended, nor shall it be construed, to release any right, title or interest in any name, trademark, trade name, advertising slogan, specification, or confidential information, but is solely intended to provide a revocable license to use the specification material for the contemplated use.

Project:
11/25/03
Section D - 1

